## Cover
GridMats® Solar Walkway
Pilot and rollout cost-benefit model
Prepared for | [Client legal entity]
Site | [Campus or site name], [City, State]
Date / prepared by | [Month Year] · GridMats (GroundReality Enterprises Pvt. Ltd.)
Scenario | Base
Headline results
Pilot
Pilot area (m²) / rated power (kWp) | 20 m² · 3.2 kWp
Generation in year 1 (kWh) | 4304.8107
Client pays, ex-GST (₹) | 182498
GridMats contribution (₹) | 345000
Pilot payback on the client's outlay (years) | 5.0558
Campus rollout
Rollout area (m²) | 1000
Installed cost (₹/sq ft) | 1080.7328
Simple payback (years) | 5.6297
IRR over 20 years | 18.19%
Comparison (same footprint)
Payback: walkway / rooftop / paver walkway + rooftop (years) | 6.6 / 3.0 / 3.5
How to use this template
1. For a new client, change the yellow cells on 'Client' (or build from clients/<id>.json with build/build.sh). Nothing else needs editing.
2. GridMats product prices and assumptions sit on 'Product & Costs'; change them only when the price list or design basis changes.
3. Pick the sunshine profile on 'Client'; replace the city row on 'Irradiance' with site data after the site assessment.
4. Blue = input · yellow fill = key assumption to confirm · black = formula · green = link to another sheet.
5. All money in ₹, ex-GST unless stated. The Solar Walkway is pre-commercial: yield, life and upkeep are estimates the pilot measures.

## Client
Client and site: [Client]
Everything that changes from one client to the next is on this sheet. Yellow cells are the ones to confirm first.
Item | Unit | Value used | Conservative | Base | Optimistic | Source / note
Scenario used across the model |  | Base | Conservative | Base | Optimistic | Switches performance ratio and degradation on 'Product & Costs'.
Scenario index |  | 2
1. Client and site
Client (short name used on slides) | text | [Client] |  |  |  | Shown on the cover and slides.
Client legal entity | text | [Client legal entity] |  |  |  | Use the entity that will issue the PO.
Campus / site | text | [Campus or site name] |  |  |  | Confirm at the site walk.
City, state | text | [City, State]
Sunshine profile (city) | choice | Bengaluru |  |  |  | Monthly sunshine from the 'Irradiance' sheet. Replace with site data after the site assessment.
Electricity supplier | text | [Electricity supplier]
Tariff category | text | [Tariff category, from the site's electricity bill] |  |  |  | Confirm from the campus electricity bill.
2. Power price and site losses
Grid power cost avoided, year 1 (landed) | ₹ / kWh | 9 |  |  |  | Placeholder: replace with the landed ₹/kWh from the site's electricity bill.
Power tariff escalation | % / yr | 3% |  |  |  | Assumption.
Site shading loss (trees, buildings) | % | 5% |  |  |  | Assumption until the site assessment measures it.
3. Pilot and rollout size
Build type | choice | New walkway |  |  |  | 'New walkway' builds the base and credits the paver walkway it replaces; 'Overlay on existing paving' levels the existing path and adds edge ramps.
Pilot walkway length | m | 10 |  |  |  | Pilots are 20-25 m².
Pilot walkway width | m | 2
Pilot area | m² | 20 |  |  |  | Length × width.
Phase 2 area (after the pilot) | m² | 200 |  |  |  | Illustrative.
Campus rollout area | m² | 1000 |  |  |  | Used on 'Rollout Economics' and 'Comparison'.
Portfolio area | m² | 5000 |  |  |  | [Other sites] (illustrative)
4. Commercial and finance
GridMats co-funding of the pilot PV layer | % | 50% |  |  |  | Pilot offer. Needs MD approval per pilot.
Discount rate | % | 10% |  |  |  | Client hurdle rate; 10% if not given.
Client income-tax rate | % | 25.17% |  |  |  | Section 115BAA rate; used for the after-tax view.
Evaluation period before the rollout decision | months | 3 |  |  |  | Earlier Jio proposal letter: 3-month pilot evaluation.
Monitoring period | months | 12 |  |  |  | Covers one monsoon.
Proposal date | text | [Month Year]
Prepared by | text | GridMats (GroundReality Enterprises Pvt. Ltd.)

## Product & Costs
GridMats Solar Walkway: product and cost assumptions
Standard GridMats inputs, the same for every client. ₹ shown per sq ft first, then per m², ex-GST.
Assumption | Unit | Value used | Conservative | Base | Optimistic | Source / note
1. Product: module technology and rated power
Cell technology of the walkable module | choice | TOPCon (n-type) |  |  |  | Pick from the 'Module Tech' library. Drives temperature loss and degradation; confirm with the module supplier's datasheet.
Rated-power basis | choice | Design basis (40 W per module) |  |  |  | Design basis = the MD-approved 40 W per module. 'Technology-derived' rates the module from its cell technology (upgrade path, to be validated).
Design-basis module rated power | Wp | 40 |  |  |  | GridMats Solar Walkway flier (6 Oct 2026) and Client/Partner Deck v2.
Modules per m² of walkway (one on each 500 × 500 mm grid) | nos / m² | 4 |  |  |  | Flier (6 Oct 2026): 4 grids per m².
Module length | mm | 550 |  |  |  | Client/Partner Deck v2.
Module width | mm | 400 |  |  |  | Client/Partner Deck v2.
Module area | m² | 0.22 |  |  |  | Length × width.
Cell efficiency, mass production (selected technology) | % | 25.8% |  |  |  | From 'Module Tech'.
Standard module efficiency (selected technology) | % | 23.5% |  |  |  | From 'Module Tech'.
Temperature coefficient of power | % / °C | -0.29% |  |  |  | From 'Module Tech'.
First-year degradation | % | 1% |  |  |  | From 'Module Tech'.
Annual degradation after year 1 | % / yr | 0.4% |  |  |  | From 'Module Tech'.
Walk-on build loss vs a standard module (thick textured glass, lower cell packing) | % | 15% |  |  |  | Assumption for the technology-derived rating. The 40 W design basis implies about 23% on a 23.5% TOPCon module.
Technology-derived module rating | Wp | 43.945 |  |  |  | Module area × efficiency × (1 − walk-on loss).
Module rated power used | Wp | 40 |  |  |  | Per the rated-power basis above.
Rated power of the walkway | Wp / m² | 160 |  |  |  | About 160 W/m² on the design basis (flier, 6 Oct 2026).
Walkway module efficiency (check) | % | 18.18% |  |  |  | Wp ÷ (module area × 1,000 W/m²).
Surface efficiency of the walkway | % | 16% |  |  |  | Flier: 15-16% surface efficiency.
2. Performance: loss stack for flat, walk-on modules
Irradiance-weighted cell temperature on the walkway | °C | 52 | 60 | 52 | 45 | Assumption. Pavement-integrated PV runs about 20 °C hotter than open-rack; GridMats' 50 mm gaps ventilate the modules.
Temperature loss | % | 7.83% |  |  |  | −temperature coefficient × (cell temperature − 25 °C).
Soiling (flat surface, foot traffic; monthly cleaning) | % | 8% | 15% | 8% | 4% | Horizontal modules soil about twice as fast as tilted ones; annual losses of 5-18% reported without frequent cleaning.
Shading by people walking on it | % | 4% | 8% | 4% | 2% | Assumption; depends on footfall at the chosen walkway.
Reflection and angle losses (flat, textured glass) | % | 3% | 5% | 3% | 2% | Assumption.
Mismatch and DC wiring | % | 3% | 4% | 3% | 2% | Assumption.
Inverter | % | 3.5% | 4% | 3.5% | 2.5% | Assumption.
Availability | % | 1% | 3% | 1% | 0.5% | Assumption.
Performance ratio (product of the losses above) | % | 73.17% |  |  |  | Earlier ROI model used a flat 78% (tilted C&I). Field results for road- and walk-integrated PV have been about half of rooftop yield per m²; the conservative case reflects that.
Extra degradation from walk-on use | % / yr | 0.2% | 0.4% | 0.2% | 0.1% | Assumption.
First-year degradation used | % | 1% |  |  |  | Selected technology.
Annual degradation used (technology + walk-on wear) | % / yr | 0.6% |  |  |  | Selected technology plus wear.
Analysis horizon and module life | years | 20 |  |  |  | Earlier ROI model: 20 years. Tables are built for 20 years.
Inverter replacement | ₹ / kWp | 4000 |  |  |  | Assumption.
Inverter replacement year | year | 12 |  |  |  | Assumption.
Annual O&M (cleaning, inspection, minor repairs) | % of capex / yr | 1.5% |  |  |  | Earlier ROI model.
3. Prices and costs (ex-GST)
Walkable PV layer, pilot price (12 mm toughened glass, 40 W module, MLP lumber with wiring) | ₹ / m² | 9500 |  |  |  | GridMats pilot quote (Oct 2026): ₹9,500/m² = ₹883/sq ft. Earlier ROI model's input cell used ₹2,500/m², but its own benchmark sheet and the proposal letter say ₹9,500.
Walkable PV layer, rollout price | ₹ / m² | 8500 |  |  |  | GridMats financials (Jul 2026): pricing range ₹8,000-9,000/m², midpoint ₹8,500 (= ₹790/sq ft).
Rollout price applies from | m² | 500 |  |  |  | Assumption.
MLP lumber layer, if priced separately | ₹ / m² | 0 |  |  |  | 0 when included in the PV layer. Apr 2025 calculator priced MLP at ₹150-650/m².
GridMats OC-LW 40 base grid, under 1,000 m² | ₹ / m² | 690 |  |  |  | GridMats price ladder (25 Sep 2026): ₹64/sq ft.
GridMats OC-LW 40, 1,000-2,500 m² | ₹ / m² | 650 |  |  |  | ₹60/sq ft.
GridMats OC-LW 40, 2,500-5,000 m² | ₹ / m² | 620 |  |  |  | ₹58/sq ft.
GridMats OC-LW 40, 5,000 m² and above | ₹ / m² | 590 |  |  |  | ₹55/sq ft.
New-walkway base works (subgrade, 100 mm open-graded GSB, 20 mm bedding, edges) | ₹ / m² | 268 |  |  |  | GridMats base table for pedestrian load; Design Engine 73 unit rates (60 + 160 + 36 + 12).
Overlay on existing paving (levelling, edge ramps) | ₹ / m² | 150 |  |  |  | Assumption.
Electrical BOS (inverter, cabling, combiner, protection) | ₹ / Wp | 8 |  |  |  | Earlier ROI model.
Grid integration and metering, per connection point | ₹ | 25000 |  |  |  | Earlier ROI model (pilot scale).
kWp per connection point at rollout | kWp | 50 |  |  |  | Assumption.
Logistics and freight | % of hardware | 5% |  |  |  | Earlier ROI model.
Installation labour | ₹ / m² | 300 |  |  |  | Earlier ROI model. Built by teams GridMats trains.
Paver / concrete walkway it replaces (new build only) | ₹ / m² | 1200 |  |  |  | Earlier ROI model: ₹800-1,500/m² range.
4. Pilot services (valued; offered free in the pilot)
Site assessment, shading study and engineering | ₹ | 40000 |  |  |  | Estimate of value.
GridMats supervision and training on site | days | 3 |  |  |  | Standard: up to 3 days.
Supervisor man-day rate | ₹ / day | 15000 |  |  |  | GridMats standard rate.
Supervisor travel and stay | ₹ | 40000 |  |  |  | Estimate; normally paid by the client.
IoT sensors, live dashboard and performance study for the monitoring period | ₹ | 125000 |  |  |  | Estimate of value: module-temperature and moisture sensors, reference cell, energy meter and logger, dashboard, reports.
5. Comparison benchmarks
C&I rooftop solar, all-in | ₹ / Wp | 40 |  |  |  | Earlier ROI model cost stack (₹35-45/Wp).
Rooftop / carport panel output per m² of panel | Wp / m² | 190 |  |  |  | 19% efficient panels (earlier ROI model).
Rooftop / carport performance ratio | % | 78% |  |  |  | Earlier ROI model.
Rooftop / carport annual degradation | % / yr | 0.4% |  |  |  | Same cell technology as the walkway, without walk-on wear.
Rooftop O&M | % of capex / yr | 1% |  |  |  | Earlier ROI model.
Solar carport / canopy, all-in | ₹ / Wp | 61 |  |  |  | Earlier ROI model (₹55-65/Wp).
Carport O&M | % of capex / yr | 1.2% |  |  |  | Earlier ROI model.
Conventional walkway maintenance | % of capex / yr | 2% |  |  |  | Earlier ROI model.
6. Tax and environment
GST on a solar walkway system (composite) | % | 8.9% |  |  |  | 5% on solar goods from 22 Sep 2025 (Notification 9/2025-CT(R)) on 70% of value + 18% on 30% services = 8.9%. Earlier model used 13.8%. Input tax credit on captive solar allowed per Gujarat AAR (Jan 2024); confirm for the client.
Accelerated depreciation on solar (WDV) | % | 40% |  |  |  | Income-tax Act: 40% WDV.
India grid emission factor | t CO2 / MWh | 0.71 |  |  |  | CEA CO2 Baseline Database v21.0 (FY2024-25).
Recycled PP in the OC-LW 40 base | kg / m² | 4 |  |  |  | GridMats master data.

## Module Tech
Module technology library (2026)
Pick the technology on 'Product & Costs'. TOPCon is now the mainstream cell; PERC is being phased out; Reliance makes HJT modules at Jamnagar.
| Technology | Cell efficiency (mass prod.) | Best cells (2026) | Module efficiency | Temp. coefficient (%/°C) | Year-1 degradation | Annual degradation | Module price, India (₹/Wp) | Notes | Sources
| Mono PERC (p-type) | 23.3% | Mature; no longer advancing | 21.2% | -0.35% | 2% | 0.5% | 13.8 | Being phased out; TOPCon premium over PERC has collapsed to about 0-10%. | JMK Research Apr 2026 (ex-works, 500 Wp); 2026 technology comparisons.
| TOPCon (n-type) | 25.8% | 26.66% industrial M10 cell (JinkoSolar, Feb 2026); 27.79% lab cell (ISFH-certified) | 23.5% | -0.29% | 1% | 0.4% | 14.2 | About two-thirds of global capacity; commercial modules 22.5-24.8%, best 25.91%. DCR TOPCon ₹22.3/Wp. | pv-magazine (25 Feb 2026); taiyangnews; Canadian Solar TOPHiKu6 and Jinko Tiger Neo datasheets (−0.29%/°C, 1% then 0.4%/yr); JMK Apr 2026.
| HJT (n-type) | 25.8% | Lowest temperature loss of the three | 24% | -0.25% | 1% | 0.3% | premium | Commercial modules 23-25%; price premium over TOPCon. Reliance produces HJT modules at Jamnagar. | 2026 technology comparisons (−0.24 to −0.26%/°C; 0.25-0.375%/yr).
What each technology means for this walkway (selected scenario; pilot size, same rated power)
| Technology | Temperature loss | Performance ratio | Specific yield (kWh/kWp/yr) | Pilot year-1 kWh | Pilot 20-year kWh | Technology-derived module (W) | Walkway W/m² (derived) | Reading
| Mono PERC (p-type) | 9.45% | 71.89% | 1321.6089 | 4144.5655 | 77603.8171 | 39.644 | 158.576 | PERC loses the most to heat on a hot, flat walkway.
| TOPCon (n-type) | 7.83% | 73.17% | 1345.2534 | 4261.7626 | 80547.3705 | 43.945 | 175.78 | TOPCon: the default. Lower heat loss and slower ageing than PERC at a similar price.
| HJT (n-type) | 6.75% | 74.03% | 1361.0163 | 4311.6998 | 82258.1937 | 44.88 | 179.52 | HJT: lowest heat loss; worth testing with Reliance's own Jamnagar cells.
Pilot year-1 kWh includes first-year degradation. The derived module rating is an upgrade path to be validated; the client price is quoted on the 40 W design basis.

## Irradiance
Sunshine library: monthly global horizontal irradiance (kWh/m²/day)
Pick the city on 'Client'. Values are typical-year climatology; replace with site data (Global Solar Atlas / NASA POWER) after the site walk.
| City | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | kWh/m²/yr | Avg / day | Source and confidence
| Days in month | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
| Mumbai | 4.8 | 5.6 | 6.3 | 6.7 | 6.7 | 4.6 | 3.7 | 3.8 | 4.5 | 5.1 | 4.8 | 4.6 | 1859.8 | 5.0953 | Calibrated to NASA-derived Navi Mumbai data (annual mean 5.16, Jan 4.74, Jul 3.68 kWh/m²/day) and Meteonorm 8.2 (1,814 kWh/m²/yr). Earlier ROI model: 5.3 average.
| Bengaluru | 5.4 | 6.2 | 6.6 | 6.5 | 6 | 4.8 | 4.3 | 4.6 | 5 | 4.8 | 4.6 | 4.9 | 1935.2 | 5.3019 | Indicative typical year.
| Chennai | 5 | 6 | 6.6 | 6.7 | 6.4 | 5.6 | 5.1 | 5.3 | 5.4 | 4.6 | 4 | 4.1 | 1969.1 | 5.3948 | Indicative typical year.
| Hyderabad | 5 | 5.8 | 6.4 | 6.7 | 6.6 | 5.2 | 4.5 | 4.6 | 4.9 | 4.9 | 4.7 | 4.6 | 1942 | 5.3205 | Indicative typical year.
| Delhi NCR | 3.6 | 4.6 | 5.8 | 6.7 | 7 | 6.4 | 5.4 | 5.1 | 5.3 | 4.9 | 4 | 3.4 | 1892 | 5.1836 | Indicative typical year.
| Pune | 5.2 | 6 | 6.6 | 6.8 | 6.7 | 4.8 | 3.8 | 4 | 4.7 | 5 | 4.9 | 4.8 | 1923.1 | 5.2688 | Indicative typical year.
| Ahmedabad | 4.6 | 5.4 | 6.3 | 6.9 | 7.1 | 6.2 | 4.8 | 4.6 | 5.4 | 5.3 | 4.6 | 4.3 | 1991.2 | 5.4553 | Indicative typical year.
| Jamnagar | 4.8 | 5.6 | 6.5 | 7 | 7.2 | 6.3 | 4.9 | 4.8 | 5.6 | 5.5 | 4.8 | 4.5 | 2052 | 5.6219 | Indicative typical year.
| Kolkata | 4.2 | 4.9 | 5.6 | 6.1 | 6 | 4.8 | 4.3 | 4.4 | 4.3 | 4.4 | 4.3 | 4 | 1742.1 | 4.7729 | Indicative typical year.

## Energy
Energy: what the walkway generates
Monthly generation for the pilot at the chosen city, after performance ratio and site shading.
Pilot size
Pilot area (m²) |  |  | 20
Modules |  |  | 80
Rated power (kWp) |  |  | 3.2
Sunshine profile |  |  | Bengaluru
Month | Days | Sunshine (kWh/m²/day) | Sunshine (kWh/m²/month) | Pilot generation (kWh) | Per m² (kWh) | Per day (kWh)
Jan | 31 | 5.4 | 167.4 | 372.3777 | 18.6189 | 12.0122
Feb | 28 | 6.2 | 173.6 | 386.1695 | 19.3085 | 13.7918
Mar | 31 | 6.6 | 204.6 | 455.1283 | 22.7564 | 14.6816
Apr | 30 | 6.5 | 195 | 433.7733 | 21.6887 | 14.4591
May | 31 | 6 | 186 | 413.753 | 20.6876 | 13.3469
Jun | 30 | 4.8 | 144 | 320.3249 | 16.0162 | 10.6775
Jul | 31 | 4.3 | 133.3 | 296.523 | 14.8261 | 9.5653
Aug | 31 | 4.6 | 142.6 | 317.2106 | 15.8605 | 10.2326
Sep | 30 | 5 | 150 | 333.6718 | 16.6836 | 11.1224
Oct | 31 | 4.8 | 148.8 | 331.0024 | 16.5501 | 10.6775
Nov | 30 | 4.6 | 138 | 306.978 | 15.3489 | 10.2326
Dec | 31 | 4.9 | 151.9 | 337.8983 | 16.8949 | 10.8999
Year 1* | 365 |  | 1935.2 | 4304.8107 | 215.2405 | 11.794
* Before first-year degradation; the cash-flow sheets apply it.
Key energy figures
Specific yield (kWh per kWp per year) |  |  | 1345.2534
Generation per m² per day, average (kWh) |  |  | 0.5897
Best month (kWh) |  |  | 455.1283
Weakest month (kWh) |  |  | 296.523
CO2 avoided in year 1 (kg) |  |  | 3056.4156
Recycled PP in the pilot base (kg) |  |  | 80

## Pilot BoQ
Pilot bill of quantities and offer
List = GridMats standard value. 'GridMats contributes' = what the pilot offer covers. Ex-GST unless stated.
Item | Qty | Unit | Rate (₹) | List value (₹) | GridMats contributes (₹) | Client pays (₹) | Note
Site assessment, shading study and engineering design | 1 | lot | 40000 | 40000 | 40000 | 0 | Included
Base works: new walkway (subgrade, open-graded GSB, bedding, edges) or overlay levelling and ramps | 20 | m² | 268 | 5360 | 0 | 5360
GridMats OC-LW 40 structural base (100% recycled PP), 4 grids per m² | 20 | m² | 690 | 13800 | 0 | 13800
Walkable PV layer: 40 W modules, 12 mm toughened glass, MLP lumber with wiring | 20 | m² | 9500 | 190000 | 95000 | 95000 | Co-funded by GridMats
MLP lumber layer (only if priced separately) | 20 | m² | 0 | 0 | 0 | 0
Electrical BOS: inverter, DC/AC cabling, protection, earthing | 3200 | Wp | 8 | 25600 | 0 | 25600
Logistics and freight | 234760 | ₹ | 5% | 11738 | 0 | 11738 | % of hardware
Grid integration and metering | 1 | lot | 25000 | 25000 | 0 | 25000
Installation labour | 20 | m² | 300 | 6000 | 0 | 6000 | Built by teams GridMats trains
GridMats supervision and training on site | 3 | days | 15000 | 45000 | 45000 | 0 | Included
Supervisor travel and stay | 1 | lot | 40000 | 40000 | 40000 | 0 | Included
IoT sensors, live dashboard and performance study | 1 | lot | 125000 | 125000 | 125000 | 0 | Included
Total (ex-GST) |  |  |  | 527498 | 345000 | 182498
GST on what the client pays |  |  | 8.9% |  |  | 16242.322
Client pays, including GST | [5 empty] | 198740.322
Summary
Physical installed cost of the pilot, list (hardware, logistics, integration, installation) | [5 empty] | 277498
Physical installed cost per sq ft (₹) | [5 empty] | 1289.0216
Physical installed cost per m² (₹) | [5 empty] | 13874.9
Physical installed cost per kWp (₹) | [5 empty] | 86718.125
Client pays per sq ft, ex-GST (₹) | [5 empty] | 847.7318
GridMats contribution as a share of list | [5 empty] | 65.4%
PV layer price per sq ft, pilot (₹) | [5 empty] | 882.5797

## Pilot Economics
Pilot economics
Two views: on what the client actually pays (with GridMats co-funding), and on the full physical cost (no co-funding).
Client's pilot outlay, ex-GST (₹) | [6 empty] | 182498
Full physical installed cost, ex-GST (₹) | [6 empty] | 277498
Year-1 generation (kWh) | [6 empty] | 4304.8107
O&M is charged on the physical installed cost in both views. GST is excluded on the assumption that the client claims input tax credit.
A. On the client's outlay (pilot offer)
Year | Degradation factor | Generation (kWh) | Tariff (₹/kWh) | Savings (₹) | O&M (₹) | Inverter (₹) | Net cash flow (₹) | Cumulative (₹) | Discount factor | Discounted CF (₹) | Cumulative discounted (₹)
0 | [6 empty] | -182498 | -182498 | 1 | -182498 | -182498
1 | 0.99 | 4261.7626 | 9 | 38355.8638 | -4162.47 | 0 | 34193.3938 | -148304.6062 | 0.90909 | 31084.9034 | -151413.0966
2 | 0.98406 | 4236.1921 | 9.27 | 39269.5004 | -4162.47 | 0 | 35107.0304 | -113197.5758 | 0.82645 | 29014.0747 | -122399.0218
3 | 0.97816 | 4210.7749 | 9.5481 | 40204.8999 | -4162.47 | 0 | 36042.4299 | -77155.1459 | 0.75131 | 27079.2111 | -95319.8108
4 | 0.97229 | 4185.5103 | 9.8345 | 41162.5807 | -4162.47 | 0 | 37000.1107 | -40155.0352 | 0.68301 | 25271.5734 | -70048.2373
5 | 0.96645 | 4160.3972 | 10.1296 | 42143.0733 | -4162.47 | 0 | 37980.6033 | -2174.4319 | 0.62092 | 23582.9665 | -46465.2709
6 | 0.96065 | 4135.4348 | 10.4335 | 43146.9213 | -4162.47 | 0 | 38984.4513 | 36810.0194 | 0.56447 | 22005.7065 | -24459.5644
7 | 0.95489 | 4110.6222 | 10.7465 | 44174.681 | -4162.47 | 0 | 40012.211 | 76822.2304 | 0.51316 | 20532.5909 | -3926.9735
8 | 0.94916 | 4085.9585 | 11.0689 | 45226.9219 | -4162.47 | 0 | 41064.4519 | 117886.6823 | 0.46651 | 19156.8699 | 15229.8963
9 | 0.94347 | 4061.4427 | 11.4009 | 46304.2272 | -4162.47 | 0 | 42141.7572 | 160028.4395 | 0.4241 | 17872.2189 | 33102.1152
10 | 0.93781 | 4037.0741 | 11.743 | 47407.1939 | -4162.47 | 0 | 43244.7239 | 203273.1634 | 0.38554 | 16672.7131 | 49774.8283
11 | 0.93218 | 4012.8516 | 12.0952 | 48536.4332 | -4162.47 | 0 | 44373.9632 | 247647.1266 | 0.35049 | 15552.8034 | 65327.6317
12 | 0.92659 | 3988.7745 | 12.4581 | 49692.5711 | -4162.47 | -12800 | 32730.1011 | 280377.2277 | 0.31863 | 10428.8189 | 75756.4506
13 | 0.92103 | 3964.8419 | 12.8318 | 50876.2481 | -4162.47 | 0 | 46713.7781 | 327091.0058 | 0.28966 | 13531.3176 | 89287.7681
14 | 0.9155 | 3941.0528 | 13.2168 | 52088.1203 | -4162.47 | 0 | 47925.6503 | 375016.6561 | 0.26333 | 12620.3216 | 101908.0897
15 | 0.91001 | 3917.4065 | 13.6133 | 53328.8594 | -4162.47 | 0 | 49166.3894 | 424183.0455 | 0.23939 | 11770.0427 | 113678.1325
16 | 0.90455 | 3893.9021 | 14.0217 | 54599.1528 | -4162.47 | 0 | 50436.6828 | 474619.7283 | 0.21763 | 10976.4917 | 124654.6241
17 | 0.89912 | 3870.5386 | 14.4424 | 55899.7046 | -4162.47 | 0 | 51737.2346 | 526356.9629 | 0.19784 | 10235.9361 | 134890.5602
18 | 0.89372 | 3847.3154 | 14.8756 | 57231.2356 | -4162.47 | 0 | 53068.7656 | 579425.7285 | 0.17986 | 9544.884 | 144435.4442
19 | 0.88836 | 3824.2315 | 15.3219 | 58594.4836 | -4162.47 | 0 | 54432.0136 | 633857.7421 | 0.16351 | 8900.0692 | 153335.5133
20 | 0.88303 | 3801.2861 | 15.7816 | 59990.2042 | -4162.47 | 0 | 55827.7342 | 689685.4763 | 0.14864 | 8298.437 | 161633.9503
Results: client's outlay
Year-1 generation (kWh) |  |  |  | 4261.7626
Year-1 savings (₹) |  |  |  | 38355.8638
Year-1 O&M (₹) |  |  |  | 4162.47
Simple payback (years) |  |  |  | 5.0558
Discounted payback (years) |  |  |  | 7.205
NPV over 20 years (₹) |  |  |  | 161633.9503
IRR over 20 years |  |  |  | 20.49%
20-year net cash (₹) |  |  |  | 689685.4763
Return on investment over 20 years (×) |  |  |  | 3.7791
B. On the full physical installed cost (no co-funding)
Year | Degradation factor | Generation (kWh) | Tariff (₹/kWh) | Savings (₹) | O&M (₹) | Inverter (₹) | Net cash flow (₹) | Cumulative (₹) | Discount factor | Discounted CF (₹) | Cumulative discounted (₹)
0 | [6 empty] | -277498 | -277498 | 1 | -277498 | -277498
1 | 0.99 | 4261.7626 | 9 | 38355.8638 | -4162.47 | 0 | 34193.3938 | -243304.6062 | 0.90909 | 31084.9034 | -246413.0966
2 | 0.98406 | 4236.1921 | 9.27 | 39269.5004 | -4162.47 | 0 | 35107.0304 | -208197.5758 | 0.82645 | 29014.0747 | -217399.0218
3 | 0.97816 | 4210.7749 | 9.5481 | 40204.8999 | -4162.47 | 0 | 36042.4299 | -172155.1459 | 0.75131 | 27079.2111 | -190319.8108
4 | 0.97229 | 4185.5103 | 9.8345 | 41162.5807 | -4162.47 | 0 | 37000.1107 | -135155.0352 | 0.68301 | 25271.5734 | -165048.2373
5 | 0.96645 | 4160.3972 | 10.1296 | 42143.0733 | -4162.47 | 0 | 37980.6033 | -97174.4319 | 0.62092 | 23582.9665 | -141465.2709
6 | 0.96065 | 4135.4348 | 10.4335 | 43146.9213 | -4162.47 | 0 | 38984.4513 | -58189.9806 | 0.56447 | 22005.7065 | -119459.5644
7 | 0.95489 | 4110.6222 | 10.7465 | 44174.681 | -4162.47 | 0 | 40012.211 | -18177.7696 | 0.51316 | 20532.5909 | -98926.9735
8 | 0.94916 | 4085.9585 | 11.0689 | 45226.9219 | -4162.47 | 0 | 41064.4519 | 22886.6823 | 0.46651 | 19156.8699 | -79770.1037
9 | 0.94347 | 4061.4427 | 11.4009 | 46304.2272 | -4162.47 | 0 | 42141.7572 | 65028.4395 | 0.4241 | 17872.2189 | -61897.8848
10 | 0.93781 | 4037.0741 | 11.743 | 47407.1939 | -4162.47 | 0 | 43244.7239 | 108273.1634 | 0.38554 | 16672.7131 | -45225.1717
11 | 0.93218 | 4012.8516 | 12.0952 | 48536.4332 | -4162.47 | 0 | 44373.9632 | 152647.1266 | 0.35049 | 15552.8034 | -29672.3683
12 | 0.92659 | 3988.7745 | 12.4581 | 49692.5711 | -4162.47 | -12800 | 32730.1011 | 185377.2277 | 0.31863 | 10428.8189 | -19243.5494
13 | 0.92103 | 3964.8419 | 12.8318 | 50876.2481 | -4162.47 | 0 | 46713.7781 | 232091.0058 | 0.28966 | 13531.3176 | -5712.2319
14 | 0.9155 | 3941.0528 | 13.2168 | 52088.1203 | -4162.47 | 0 | 47925.6503 | 280016.6561 | 0.26333 | 12620.3216 | 6908.0897
15 | 0.91001 | 3917.4065 | 13.6133 | 53328.8594 | -4162.47 | 0 | 49166.3894 | 329183.0455 | 0.23939 | 11770.0427 | 18678.1325
16 | 0.90455 | 3893.9021 | 14.0217 | 54599.1528 | -4162.47 | 0 | 50436.6828 | 379619.7283 | 0.21763 | 10976.4917 | 29654.6241
17 | 0.89912 | 3870.5386 | 14.4424 | 55899.7046 | -4162.47 | 0 | 51737.2346 | 431356.9629 | 0.19784 | 10235.9361 | 39890.5602
18 | 0.89372 | 3847.3154 | 14.8756 | 57231.2356 | -4162.47 | 0 | 53068.7656 | 484425.7285 | 0.17986 | 9544.884 | 49435.4442
19 | 0.88836 | 3824.2315 | 15.3219 | 58594.4836 | -4162.47 | 0 | 54432.0136 | 538857.7421 | 0.16351 | 8900.0692 | 58335.5133
20 | 0.88303 | 3801.2861 | 15.7816 | 59990.2042 | -4162.47 | 0 | 55827.7342 | 594685.4763 | 0.14864 | 8298.437 | 66633.9503
Results: full physical cost
Year-1 generation (kWh) |  |  |  | 4261.7626
Year-1 savings (₹) |  |  |  | 38355.8638
Year-1 O&M (₹) |  |  |  | 4162.47
Simple payback (years) |  |  |  | 7.4427
Discounted payback (years) |  |  |  | 13.4526
NPV over 20 years (₹) |  |  |  | 66633.9503
IRR over 20 years |  |  |  | 13.07%
20-year net cash (₹) |  |  |  | 594685.4763
Return on investment over 20 years (×) |  |  |  | 2.143

## Rollout Economics
Rollout economics: campus walkway at rollout prices
Uses the campus rollout area from 'Client'. No co-funding at rollout.
Installed cost per m² at the rollout area
Rollout area (m²) | [6 empty] | 1000
Rated power (kWp) | [6 empty] | 160
Base works (₹/m²) | [6 empty] | 268
GridMats OC-LW 40 at this area (₹/m²) | [6 empty] | 650
Walkable PV layer (₹/m²) | [6 empty] | 8500
Electrical BOS (₹/m²) | [6 empty] | 1280
Logistics (₹/m²) | [6 empty] | 534.9
Grid integration (₹/m²) | [6 empty] | 100
Installation (₹/m²) | [6 empty] | 300
Installed cost (₹/m²) | [6 empty] | 11632.9
Installed cost (₹/sq ft) | [6 empty] | 1080.7328
Less: walkway it replaces (₹/m², new build only) | [6 empty] | 1200
Net extra cost for a generating walkway (₹/m²) | [6 empty] | 10432.9
Total installed cost (₹) | [6 empty] | 11632900
Net investment after walkway credit (₹) | [6 empty] | 10432900
Year-1 generation (kWh) | [6 empty] | 215240.5374
Installed cost per kWp, solar part (₹) | [6 empty] | 65093.125
Year | Degradation factor | Generation (kWh) | Tariff (₹/kWh) | Savings (₹) | O&M (₹) | Inverter (₹) | Net cash flow (₹) | Cumulative (₹) | Discount factor | Discounted CF (₹) | Cumulative discounted (₹)
0 | [6 empty] | -10432900 | -10432900 | 1 | -10432900 | -10432900
1 | 0.99 | 213088.132 | 9 | 1917793.188 | -174493.5 | 0 | 1743299.688 | -8689600.312 | 0.90909 | 1584817.8982 | -8848082.1018
2 | 0.98406 | 211809.6032 | 9.27 | 1963475.0218 | -174493.5 | 0 | 1788981.5218 | -6900618.7902 | 0.82645 | 1478497.1254 | -7369584.9764
3 | 0.97816 | 210538.7456 | 9.5481 | 2010244.9968 | -174493.5 | 0 | 1835751.4968 | -5064867.2935 | 0.75131 | 1379227.2703 | -5990357.7061
4 | 0.97229 | 209275.5131 | 9.8345 | 2058129.0326 | -174493.5 | 0 | 1883635.5326 | -3181231.7609 | 0.68301 | 1286548.4138 | -4703809.2923
5 | 0.96645 | 208019.86 | 10.1296 | 2107153.6662 | -174493.5 | 0 | 1932660.1662 | -1248571.5947 | 0.62092 | 1200029.9074 | -3503779.3849
6 | 0.96065 | 206771.7409 | 10.4335 | 2157346.0665 | -174493.5 | 0 | 1982852.5665 | 734280.9718 | 0.56447 | 1119268.5809 | -2384510.804
7 | 0.95489 | 205531.1104 | 10.7465 | 2208734.0498 | -174493.5 | 0 | 2034240.5498 | 2768521.5216 | 0.51316 | 1043887.0526 | -1340623.7515
8 | 0.94916 | 204297.9238 | 11.0689 | 2261346.0948 | -174493.5 | 0 | 2086852.5948 | 4855374.1164 | 0.46651 | 973532.1369 | -367091.6145
9 | 0.94347 | 203072.1362 | 11.4009 | 2315211.3588 | -174493.5 | 0 | 2140717.8588 | 6996091.9752 | 0.4241 | 907873.3455 | 540781.731
10 | 0.93781 | 201853.7034 | 11.743 | 2370359.6934 | -174493.5 | 0 | 2195866.1934 | 9191958.1686 | 0.38554 | 846601.4753 | 1387383.2063
11 | 0.93218 | 200642.5812 | 12.0952 | 2426821.6613 | -174493.5 | 0 | 2252328.1613 | 11444286.3299 | 0.35049 | 789427.2802 | 2176810.4865
12 | 0.92659 | 199438.7257 | 12.4581 | 2484628.5533 | -174493.5 | -640000 | 1670135.0533 | 13114421.3832 | 0.31863 | 532156.4977 | 2708966.9842
13 | 0.92103 | 198242.0933 | 12.8318 | 2543812.4054 | -174493.5 | 0 | 2369318.9054 | 15483740.2886 | 0.28966 | 686307.2911 | 3395274.2753
14 | 0.9155 | 197052.6408 | 13.2168 | 2604406.0169 | -174493.5 | 0 | 2429912.5169 | 17913652.8055 | 0.26333 | 639871.9109 | 4035146.1863
15 | 0.91001 | 195870.3249 | 13.6133 | 2666442.9682 | -174493.5 | 0 | 2491949.4682 | 20405602.2737 | 0.23939 | 596552.8901 | 4631699.0764
16 | 0.90455 | 194695.103 | 14.0217 | 2729957.6397 | -174493.5 | 0 | 2555464.1397 | 22961066.4134 | 0.21763 | 556143.4523 | 5187842.5287
17 | 0.89912 | 193526.9324 | 14.4424 | 2794985.2307 | -174493.5 | 0 | 2620491.7307 | 25581558.1441 | 0.19784 | 518450.3188 | 5706292.8475
18 | 0.89372 | 192365.7708 | 14.8756 | 2861561.7789 | -174493.5 | 0 | 2687068.2789 | 28268626.423 | 0.17986 | 483292.849 | 6189585.6965
19 | 0.88836 | 191211.5762 | 15.3219 | 2929724.1805 | -174493.5 | 0 | 2755230.6805 | 31023857.1035 | 0.16351 | 450502.2328 | 6640087.9294
20 | 0.88303 | 190064.3067 | 15.7816 | 2999510.2105 | -174493.5 | 0 | 2825016.7105 | 33848873.814 | 0.14864 | 419920.7331 | 7060008.6624
Results: campus rollout
Year-1 generation (kWh) |  |  |  | 213088.132
Year-1 savings (₹) |  |  |  | 1917793.188
Year-1 O&M (₹) |  |  |  | 174493.5
Simple payback (years) |  |  |  | 5.6297
Discounted payback (years) |  |  |  | 8.4043
NPV over 20 years (₹) |  |  |  | 7060008.6624
IRR over 20 years |  |  |  | 18.19%
20-year net cash (₹) |  |  |  | 33848873.814
Return on investment over 20 years (×) |  |  |  | 3.2444
After-tax view with 40% accelerated depreciation on the solar part
Year | Opening WDV (₹) | Depreciation (₹) | Tax shield (₹) | After-tax cash flow (₹)
0 | 0 | 0 | 0 | -10432900
1 | 10414900 | 4165960 | 1048572.132 | 2353083.2885
2 | 6248940 | 2499576 | 629143.2792 | 1967838.1519
3 | 3749364 | 1499745.6 | 377485.9675 | 1751178.8126
4 | 2249618.4 | 899847.36 | 226491.5805 | 1636016.0496
5 | 1349771.04 | 539908.416 | 135894.9483 | 1582104.5506
6 | 809862.624 | 323945.0496 | 81536.969 | 1565305.5445
7 | 485917.5744 | 194367.0298 | 48922.1814 | 1571144.3848
8 | 291550.5446 | 116620.2179 | 29353.3088 | 1590945.1056
9 | 174930.3268 | 69972.1307 | 17611.9853 | 1619511.1591
10 | 104958.1961 | 41983.2784 | 10567.1912 | 1653733.8637
11 | 62974.9176 | 25189.9671 | 6340.3147 | 1691757.4778
12 | 37784.9506 | 15113.9802 | 3804.1888 | 1253566.2492
13 | 22670.9704 | 9068.3881 | 2282.5133 | 1775243.8502
14 | 13602.5822 | 5441.0329 | 1369.508 | 1819673.0444
15 | 8161.5493 | 3264.6197 | 821.7048 | 1865547.4919
16 | 4896.9296 | 1958.7718 | 493.0229 | 1912746.8386
17 | 2938.1578 | 1175.2631 | 295.8137 | 1961209.7758
18 | 1762.8947 | 705.1579 | 177.4882 | 2010910.6813
19 | 1057.7368 | 423.0947 | 106.4929 | 2061845.6111
20 | 634.6421 | 253.8568 | 63.8958 | 2114023.9002
After-tax IRR |  |  |  | 16.48%
Levelised cost of the walkway's power (₹/kWh) |  |  |  | 6.9353

## Comparison
How it compares on the same footprint
Rollout area from 'Client'. A replaces a walkway and generates; D is the business-as-usual pair it should be compared with.
Metric | A. GridMats Solar Walkway | B. Rooftop solar | C. Solar carport | D. Paver walkway + rooftop | Year | PVF walkway | PVF rooftop
[5 empty] | 1 | 0.9 | 0.9
Footprint (m²) | 1000 | 1000 | 1000 | 1000 | 2 | 0.83767 | 0.83936
Installed capacity (kWp) | 160 | 190 | 190 | 190 | 3 | 0.77966 | 0.7828
Total capex (₹) | 11632900 | 7600000 | 11590000 | 8800000 | 4 | 0.72566 | 0.73005
Capex per kWp (₹) | 72705.625 | 40000 | 61000 | 46315.7895 | 5 | 0.67541 | 0.68086
Year-1 generation (kWh) | 215240.5374 | 286796.64 | 286796.64 | 286796.64 | 6 | 0.62863 | 0.63498
Year-1 savings (₹) | 1937164.8364 | 2581169.76 | 2581169.76 | 2581169.76 | 7 | 0.5851 | 0.5922
Year-1 O&M (₹) | 174493.5 | 76000 | 139080 | 100000 | 8 | 0.54458 | 0.55229
Simple payback on year-1 figures (years) | 6.5996 | 3.0337 | 4.7459 | 3.5467 | 9 | 0.50686 | 0.51508
NPV over 20 years (₹) | 6063932.3858 | 17686252.3634 | 13159216.764 | 16281926.8341 | 10 | 0.47176 | 0.48037
Provides a walking surface | Yes | No | Shade, not a walkway | Yes | 11 | 0.43909 | 0.448
Needs roof or extra structure | No | Roof | Steel canopy and footings | Roof | 12 | 0.40868 | 0.41782
Recycled plastic in the structure (t) | 4 | 0 | 0 | 0 | 13 | 0.38038 | 0.38966
[5 empty] | 14 | 0.35403 | 0.36341
Rooftop and carport figures are the earlier ROI model's benchmarks. Rooftop is cheaper per kWp; the walkway earns its place where roofs are full, shaded or carry plant, and where a walkway is being built or relaid anyway (compare A with D). |  |  |  |  | 15 | 0.32952 | 0.33892
[5 empty] | 16 | 0.30669 | 0.31608
[5 empty] | 17 | 0.28545 | 0.29478
[5 empty] | 18 | 0.26569 | 0.27492
[5 empty] | 19 | 0.24729 | 0.2564
[5 empty] | 20 | 0.23016 | 0.23912
[5 empty] | Σ | 9.9023 | 10.0471
[5 empty] | Annuity | 8.5136

## Sensitivity
Sensitivity: rollout payback (years)
Simple payback on year-1 figures for the campus rollout. Each table varies two inputs and keeps the rest.
Power price × performance ratio
₹ / kWh ↓ / Performance ratio → | 60% | 65% | 70% | 75% | 80%
8 | 8.4311 | 7.6991 | 7.084 | 6.5599 | 6.108
9 | 7.3787 | 6.7471 | 6.215 | 5.7608 | 5.3684
10 | 6.5599 | 6.0046 | 5.536 | 5.1352 | 4.7886
11 | 5.9046 | 5.4093 | 4.9907 | 4.6322 | 4.3218
12 | 5.3684 | 4.9215 | 4.5432 | 4.219 | 3.9379
13 | 4.9215 | 4.5143 | 4.1694 | 3.8734 | 3.6167
14 | 4.5432 | 4.1694 | 3.8524 | 3.5802 | 3.3439
Power price × rollout PV-layer price (₹/m²)
₹ / kWh ↓ / PV layer ₹/m² → | 6500 | 7500 | 8500 | 9500
8 | 5.2826 | 6.0053 | 6.7421 | 7.4933
9 | 4.6483 | 5.2782 | 5.9188 | 6.5704
10 | 4.15 | 4.7081 | 5.2747 | 5.8499
11 | 3.7482 | 4.2492 | 4.757 | 5.2719
12 | 3.4174 | 3.8718 | 4.3319 | 4.7977
13 | 3.1402 | 3.556 | 3.9765 | 4.4019
14 | 2.9046 | 3.2878 | 3.675 | 4.0664
Pilot payback on the client's outlay × GridMats co-funding
Co-funding of the PV layer → | 0% | 25% | 50% | 75%
Simple payback (years) | 8.1155 | 6.7264 | 5.3372 | 3.9481
Shading: green ≤ 6 years, amber 6-9 years, red above 9 years (applied in Excel with conditional formatting).

## Scale-up
Scale-up: from pilot to campus
Year-1 figures. Pilot uses pilot prices; later phases use the rollout prices for their area.
Measure | Pilot | Phase 2 | Campus | Portfolio | Note
Area (m²) | 20 | 200 | 1000 | 5000
Rated power (kWp) | 3.2 | 32 | 160 | 800
Generation, year 1 (MWh) | 4.3048 | 43.0481 | 215.2405 | 1076.2027
Electricity saved, year 1 (₹ lakh) | 0.38743 | 3.8743 | 19.3716 | 96.8582
CO2 avoided per year (t) | 3.0564 | 30.5642 | 152.8208 | 764.1039
Installed cost per m² (₹) | 13874.9 | 12749.9 | 11632.9 | 11549.9
Installed cost (₹ lakh) | 2.775 | 25.4998 | 116.329 | 577.495
Net of walkway credit (₹ lakh) | 2.535 | 23.0998 | 104.329 | 517.495
Simple payback on full cost (years) | 7.3306 | 6.6154 | 5.9188 | 5.8676 | Pilot column shows full physical cost, before co-funding.
Recycled PP in the base (t) | 0.08 | 0.8 | 4 | 20

## Scorecard
Pilot scorecard: measured, not assumed
Agreed with the client before installation; filled in at the evaluation review.
KPI | Target / benchmark | How it is measured | Measured result | Weight | Score (1-5) | Notes
Energy generation vs estimate | ≥ 90% of the model's monthly estimate | Energy meter and logger, monthly |  | 20%
Performance ratio achieved | ≥ PR used in the model | Generation ÷ (reference-cell irradiation × kWp) |  | 10%
Pedestrian and maintenance-cart load | 4 kN/m² uniform and 4.5 kN point load (IS 875 Part 2); no cracking or movement | Load test at handover; inspection |  | 15%
Surface temperature (peak) | Within module specification | Module-temperature sensors |  | 5%
Slip resistance and walking comfort | R11 (DIN 51130) or wet pendulum PTV ≥ 36 | Pendulum test wet and dry; user feedback |  | 10%
Drainage and water ingress | No ponding, no ingress | Inspection after heavy rain |  | 10%
Electrical uptime | ≥ 98% | Logger availability data |  | 10%
Cleaning and maintenance effort | Within O&M assumption | Cleaning log |  | 5%
Module survival and repairability | No irreparable failures | Replacement log |  | 10%
Visual finish and user acceptance | Client acceptance | Facilities and user survey |  | 5%
Weight total (must be 100%) |  |  |  | 100%
Weighted score (out of 5) |  |  |  |  | 0
KPIs and weights from the earlier GridMats Solar Walkway ROI model (Reliance / Jio R&D pilot). Fill in columns D and F at the review.

## Sources & Notes
Sources and notes
Where every number comes from, and what changed from earlier GridMats calculations.
Changes from earlier GridMats Solar Walkway calculations
Item | Earlier value (file) | This model | Why
Rated power of the walkway | 126 W/m² (ROI model: 580 × 450 mm, 82% coverage); 110 W/m² (2025 decks, flier to 6 Oct) | 160 W/m² | MD correction, 6 Oct 2026: 40 W module on each grid, 4 per m².
PV layer price | ₹2,500/m² in the ROI model's input cell | ₹9,500/m² pilot; ₹8,500/m² rollout | The ROI model's own benchmark sheet and the proposal letter state ₹9,500/m²; Jul 2026 financials give ₹8,000-9,000/m² for volume.
Structural base | GridMats HD ₹1,200/m² (ROI model) | OC-LW 40 at ₹690/m² (under 1,000 m²) | Current price ladder (25 Sep 2026); the module sits on the 500 × 500 mm grid.
Performance ratio | 78% | 70% base (62-78%) | Flat, walk-on modules run hotter and collect more dust than tilted rooftop panels.
GST | 13.8% composite | 8.9% composite (confirm) | GST on solar goods cut from 12% to 5% from 22 Sep 2025.
Power price | ₹9/kWh placeholder | Client sheet | Use the landed rate from the site's electricity bill.
Cost calculator (Apr 2025) | ₹6,540-7,800/m² at 80-111 W/m²; ₹70-84/W | Superseded | Lower power density and older module; kept for reference.
Cell technology and losses | Not modelled; flat 78% PR, 0.5%/yr | TOPCon (n-type) library; PR built from seven losses | Latest TOPCon data: −0.29%/°C, 1% then 0.4%/yr; heat and dust matter more on a flat walkway.
Sources
GridMats Solar Walkway flier (6 Oct 2026) |  |  | Design basis: 40 W per module, 4 per m², ~160 W/m², 15-16% surface efficiency; pilot method; status.
GridMats Solar Walkway Client/Partner Deck v2 |  |  | Construction (PV layer, 40 × 40 mm MLP lumber, GridMats base), 550 × 400 mm module, pilot pathway.
GridMats Solar Walkway ROI Comparison Model (Reliance / Jio R&D pilot) |  |  | Cost stack, rooftop and carport benchmarks, O&M, pilot objectives and scorecard.
GridMats Solar cost calculator (Apr 2025) |  |  | Earlier module, MLP and labour costs; superseded.
GridMats price ladder (25 Sep 2026); Design Engine 73 unit rates |  |  | OC-LW 40 prices; base-works rates.
GridMats financials (Jul 2026) |  |  | Solar walkway pricing range ₹8,000-9,000/m².
CEA CO2 Baseline Database v21.0 |  |  | Grid emission factor 0.710 t CO2/MWh.
Income-tax Act; GST Council (Sep 2025), Notification 9/2025-CT(R); Gujarat AAR GUJ/GAAR/R/2024/01 |  |  | 40% WDV depreciation; 5% GST on solar goods; ITC on captive solar.
pv-magazine (25 Feb 2026); taiyangnews; JMK Research (Apr 2026); manufacturer datasheets |  |  | TOPCon cell and module efficiency, temperature coefficient, degradation and price.
MERC order, Case 75 of 2025 (25 Mar 2026); MSEDCL circulars |  |  | HT tariffs, solar-hour ToD rebate, electricity duty.
NASA-derived Navi Mumbai climatology; Meteonorm 8.2 (ICADMSES 2026) |  |  | Mumbai sunshine calibration.
IS 875 (Part 2); DIN 51130; BS 7976-2; IS 14286 and IS/IEC 61730 (BIS) |  |  | Load, slip-resistance and module-registration targets.
Status: the GridMats Solar Walkway is pre-commercial; pilot validation is under way and no commercial deployment is claimed. Yield, life and upkeep are estimates the pilot measures.